## Slide 1: Overview of Smart Building Platform
Building Management System (BMS) Integration Proposal — March 15, 2026

## Slide 2: Building Management System
Building Management System monitors and controls the HVAC equipment.
  Control of air handling units (AHU) and fan coil units (FCU)
  Variable air volume (VAV) terminal control
Alarm and equipment status 24-hour monitoring
Energy Management System (EMS) for energy consumption analysis
Notes: The Building Management System collects data from over 2,000 points and sends alarms to operators within 5 seconds.

## Slide 3: Sensor and Field Devices
Occupancy Sensor
CO2 Sensor (0–2,000 ppm)
Temperature Sensor: Accuracy ±0.2 °C
Humidity: 30–70 %RH
Model FX-PCG2611-0 Controller, Firmware v3.2.1

## Slide 4: System Configuration
Edge Device
Gateway
Cloud Platform
Dashboard
The field controller communicates via BACnet/IP and Modbus TCP, and the gateway transmits telemetry to the cloud platform via MQTT over TLS (port 8883).

## Slide 5: Protocol Comparison
Protocol | Transport | Main Use Cases | Default Port
BACnet/IP | UDP | HVAC Controller | 47808
Modbus TCP | TCP | Electricity Meter, Chiller | 502
MQTT | TCP | IoT Telemetry to Cloud | 1883 / 8883
KNX | Twisted Pair / IP | Lighting and Blinds | 3671

## Slide 6: Energy Efficiency and Demand Response
Reduce Peak Demand by 18% in Summer 2025
Energy Consumption: 1,250 MWh/Year → 1,020 MWh/Year
Demand Response signal is received from the utility company via OpenADR 2.0b
Setpoint Adjustment: Change cooling setpoint from 24 °C to 26 °C during peak hours
Power consumption is measured every 15 minutes
Notes: Energy saving control is effective only when the occupancy rate is below 30% and the outdoor air temperature exceeds 32 °C.

## Slide 7: Network and Access
BMS Server: 192.168.1.100 (VLAN 20)
Web Dashboard: https://bms.example.com/dashboard
Support: support@example.com
Configuration File: C:\Program Files\BMS\config\points.json
HTTPS-based REST API. Payload is JSON, old format export is XML and SQL

## Slide 8: Operations and Maintenance
When an alarm occurs on the chiller, the system automatically sends an email notification to the maintenance team, creates a work order, and escalates the issue to the facility manager if the alarm is not confirmed within 30 minutes.
Regular maintenance of the air handling unit filters is performed every three months.
The PLC and SCADA systems will continue to operate during the transition period.