## Slide 1: Smart Building Platform Overview
Building Management System (BMS) Integration Proposal — 15 March 2026

## Slide 2: Building Management System
The Building Management System monitors and controls HVAC equipment.
  Air Handling Unit (AHU) and Fan Coil Unit (FCU) control
  Variable Air Volume (VAV) terminal control
Alarm and equipment status monitoring 24/7
Energy Management System (EMS) for energy consumption analysis
Notes: The building management system collects data from more than 2,000 points and sends alarms to the operator within 5 seconds.

## Slide 3: Sensors and Field Devices
Occupancy sensor
CO2 sensor (0–2,000 ppm)
Temperature sensor: ±0.2 °C accuracy
Humidity: 30–70 %RH
Model FX-PCG2611-0 controller, firmware v3.2.1

## Slide 4: System Architecture
Edge device
Gateway
Cloud platform
Dashboard
Field controllers communicate over BACnet/IP and Modbus TCP; the gateway publishes telemetry to the cloud platform via MQTT over TLS (port 8883).

## Slide 5: Protocol Comparison
Protocol | Transport | Typical use | Default port
BACnet/IP | UDP | HVAC controllers | 47808
Modbus TCP | TCP | Power meters, chillers | 502
MQTT | TCP | IoT telemetry to cloud | 1883 / 8883
KNX | Twisted pair / IP | Lighting and blinds | 3671

## Slide 6: Energy Efficiency and Demand Response
Peak demand reduced by 18% in summer 2025
Energy consumption: 1,250 MWh/year → 1,020 MWh/year
Demand response signals are received from the utility via OpenADR 2.0b
Setpoint adjustment: cooling setpoint raised from 24 °C to 26 °C during peak hours
Power consumption is measured every 15 minutes
Notes: Energy saving control is enabled only when the occupancy rate is below 30 percent and the outdoor air temperature is above 32 °C.

## Slide 7: Network and Access
BMS server: 192.168.1.100 (VLAN 20)
Web dashboard: https://bms.example.com/dashboard
Support: support@example.com
Configuration file: C:\Program Files\BMS\config\points.json
REST API over HTTPS; payloads in JSON, legacy exports in XML and SQL

## Slide 8: Operation and Maintenance
When a chiller alarm occurs, the system automatically notifies the maintenance team by e-mail and creates a work order, and if the alarm is not acknowledged within 30 minutes, it is escalated to the facility manager.
Scheduled maintenance of the AHU filters is performed every 3 months.
The PLC and SCADA system remain in service during the migration period.

## Slide 9: Building Automation Roadmap
Phase 1 (Q2 2026): Building automation system upgrade
Phase 2 (Q4 2026): IoT sensors and edge devices
Phase 3 (2027): AI-based fault detection and diagnostics (FDD)