## Slide 1: Optimization of Central Heat Plant
Improvements to the Chilled water plant and HVAC systems — 2026

## Slide 2: Overview of the Chilled water plant
The Chilled water plant supplies chilled water to 12 air handling units.
The cooling water is cooled by 3 cooling towers.
Free cooling is utilized when the outdoor air temperature is below 10 °C.
Notes: During winter, Free cooling is employed to reduce the operating time of chillers and the energy consumption of cooling water pumps.

## Slide 3: Free cooling
The Free cooling mode switches automatically.
Reduction amount through Free cooling: 210 MWh/year
Heat recovery from cooling water

## Slide 4: Supply air temperature reset
The Supply air temperature should be reset to a value within the range of 13 °C to 18 °C.
The reset is based on zone load.
The Supply air temperature setpoint is displayed on the dashboard.

## Slide 5: Fault detection and diagnosis (FDD)
Fault detection and diagnosis (FDD) is executed every 15 minutes.
The Chilled water plant and air handling unit are checked using FDD rules.
Typical faults: Damper sticking, sensor drift, simultaneous operation of heating and cooling
Notes: The results of Fault detection and diagnosis (FDD) are stored in the Trend log for 13 months.

## Slide 6: Demand-controlled ventilation
Demand-controlled ventilation utilizes CO2 sensors in conference rooms.
Demand-controlled ventilation reduces the energy used by fans by 25%.
When the ventilation volume is high, the heat recovery wheel operates.

## Slide 7: Load shedding
Load shedding is initiated by demand response events.
Order of Load shedding: lighting first, followed by demand restriction on chillers
Verify the results of Load shedding using data from the Trend log.

## Slide 8: Data Integration
The Point list contains 2,400 BACnet objects.
Trend log collection interval: 5 minutes
The Point list is exported to the cloud platform on a weekly basis.