## Slide 1: Overview of Smart Building Platform
Proposal for Integrating Building Management System (BMS) — March 15, 2026

## Slide 2: Building Management System
The Building Management System monitors and controls HVAC systems.
  Control of air handling units (AHU) and fan coil units (FCU)
  Variable air volume (VAV) terminal control
24/7 monitoring of alarm and equipment status
Energy Management System (EMS) for energy consumption analysis
Notes: The Building Management System collects data from over 2,000 monitoring points and sends alarms to operators within 5 seconds.

## Slide 3: Sensors and Field Devices
Occupancy sensor
CO2 sensor (0–2,000 ppm)
Temperature sensor: Accuracy ±0.2 °C
Humidity: 30–70 %RH
Model FX-PCG2611-0 controller, firmware v3.2.1

## Slide 4: System Architecture
Edge device
Gateway
Cloud platform
Dashboard
The field controller communicates using BACnet/IP and Modbus TCP, while the gateway sends Telemetry to the cloud platform via MQTT over TLS (port 8883).

## Slide 5: Protocol Comparison
Protocol | Transport | Primary Uses | Default Port
BACnet/IP | UDP | Air conditioning controller | 47808
Modbus TCP | TCP | Power meter, chiller | 502
MQTT | TCP | IoT Telemetry to the Cloud | 1883 / 8883
KNX | Twisted Pair / IP | Lighting and blinds | 3671

## Slide 6: Energy-saving mode and Demand Response
Reduce peak demand by 18% by the summer of 2025
Energy consumption: 1,250 MWh/year → 1,020 MWh/year
Demand Response signals are received from power companies via OpenADR 2.0b.
Setpoint adjustment: Change the air conditioning setpoint from 24 °C to 26 °C during peak hours
Power consumption is measured every 15 minutes.
Notes: The Energy-saving mode is activated only when the occupancy rate is below 30% and the outdoor air temperature exceeds 32 °C.

## Slide 7: Networks and Access
BMS server: 192.168.1.100 (VLAN 20)
Web dashboard: https://bms.example.com/dashboard
Support: support@example.com
Configuration file: C:\Program Files\BMS\config\points.json
REST API over HTTPS. The payload is JSON, while legacy exports use XML and SQL.

## Slide 8: Operation & Maintenance
When an alarm is triggered on a chiller, the system automatically sends an email notification to the maintenance team to create a work order. If the alarm is not resolved within 30 minutes, it is escalated to the facility manager.
Regular maintenance for air handling unit filters is carried out every 3 months.
The PLC and SCADA systems will continue to operate throughout the transition period.