## Slide 1: Optimization of Central Heat Plant
Improvements to chilled water plants and HVAC systems — 2026

## Slide 2: Overview of the chilled water plant
The chilled water plant supplies chilled water to 12 air handling units.
The cooling water is cooled by 3 cooling towers.
Free cooling is utilized when the outdoor air temperature is below 10 °C.
Notes: During winter, free cooling helps reduce the operating time of chillers and the energy consumption of cooling water pumps.

## Slide 3: Free Cooling
The free cooling mode switches automatically.
Reduction achieved through free cooling: 210 MWh/year
Heat recovery from cooling water

## Slide 4: Supply Air Temperature Reset
The supply air temperature is reset to a range of 13 °C to 18 °C.
The reset is based on zone load.
The supply air temperature setpoint is displayed on the dashboard.

## Slide 5: Fault Detection and Diagnosis (FDD)
Fault Detection and Diagnosis (FDD) is executed every 15 minutes.
The FDD rules are used to check the chilled water plant and air handling units.
Typical faults: damper sticking, sensor drift, simultaneous operation of heating and cooling.
Notes: The results of Fault Detection and Diagnosis (FDD) are stored in the trend log for 13 months.

## Slide 6: Demand-controlled ventilation
Demand-controlled ventilation uses a CO2 sensor in conference rooms.
Demand-controlled ventilation reduces fan energy consumption by 25%.
When ventilation volume is high, the heat recovery wheel operates.

## Slide 7: Load Shutoff
Load Shutoff is initiated by demand response events.
Sequence of Load Shutoff: lighting first, followed by demand restriction on chillers
Verify the results of the Load Shutoff using data from the trend log.

## Slide 8: Data Integration
The point list contains 2,400 BACnet objects.
Trend log collection interval: 5 minutes
The point list is exported to the cloud platform weekly.