## Slide 1: Central Plant Optimisation
Chilled water plant and air-side improvements — 2026

## Slide 2: Chilled Water Plant Overview
The chilled water plant serves 12 air handling units.
Condenser water is cooled by three cooling towers.
Free cooling is used when the outdoor air temperature is below 10 °C.
Notes: During winter, free cooling reduces chiller operating hours and condenser water pump energy.

## Slide 3: Free Cooling
Free cooling mode switches automatically
Free cooling savings: 210 MWh/year
Heat recovery from condenser water

## Slide 4: Supply Air Temperature Reset
Supply air temperature is reset between 13 °C and 18 °C
The reset is based on zone demand
Supply air temperature setpoint is shown on the dashboard

## Slide 5: Fault Detection and Diagnostics (FDD)
Fault detection and diagnostics runs every 15 minutes.
FDD rules check the chilled water plant and air handling units.
Typical faults: stuck damper, sensor drift, simultaneous heating and cooling
Notes: Fault detection and diagnostics results are stored in the trend log for 13 months.

## Slide 6: Demand-Controlled Ventilation
Demand-controlled ventilation uses CO2 sensors in meeting rooms.
Demand-controlled ventilation reduces fan energy by 25%.
Heat recovery wheels operate when ventilation rates are high.

## Slide 7: Load Shedding
Load shedding is triggered by demand response events.
Load shedding sequence: lighting, then chiller demand limit
Trend log data verifies the load shedding result.

## Slide 8: Data and Integration
The point list contains 2,400 BACnet objects.
Trend log interval: 5 minutes
The point list is exported to the cloud platform weekly.